## SBFF Pump 1
Pump Station / No: | SBFFPS | #1 |  |  |  |  | Manufacturer Pump Curve |  |  |  | Test Pump Curve Transposed for Model Use
|  |  | Pump Mfr: | Floway |  |  | TDH (ft) | Flow (mgd) | Flow (gpm) | Bowl Eff (%) | Test Pt | Total Head (ft): | Discharge Flow (mgd): | Overall Pump Efficiency:
Design Point |  |  | Pump Model: | 22BKL |  | 1 | 202.89 | 0 | 0 | 0% | 1 |  | 0
MGD | 8.0064 |  | Serial Number: | 78639-1-1 |  | 2 | 164.97 | 3.0941 | 2148.69 | 41.87% | 2 |  | 0
GPM | 5560 |  | Pump Installed: | 2018 |  | 3 | 151.58 | 4.5163 | 3136.33 | 57.49% | 3 |  | 0
TDH (FT) | 120 |  | Motor HP: | 250 |  | 4 | 135.3 | 5.8827 | 4085.22 | 68.49% | 4 |  | 0
|  |  | Motor Voltage: | 4160 |  | 5 | 130.82 | 6.4437 | 4474.77 | 72.37% | 5 |  | 0
Elevation Information |  |  | Motor Installed: | 2018 |  | 6 | 125 | 7.2676 | 5046.93 | 77.07% | 6 |  | 0
Pump Disch Hdr CL Elev (ft): | 1473 |  | RPM: | 1785 |  | 7 | 123.04 | 8.0114 | 5563.5 | 81.71% | 7 |  | 0
Reservoir Floor Elev (ft): | 1444.5 |  | Power Factor: | 0.8 |  | 8 | 117.22 | 8.8218 | 6126.27 | 83.59% | 8 |  | 0
Suction Header CL Elev (ft): | NA |  | Motor Efficiency: | 0.9 |  | 9 | 91.43 | 10.7215 | 7445.47 | 79.49% | 9 |  | 0
Service Zone: | Falcon Field |  |  |  |  | 10 | 56.06 | 12.5997 | 8749.77 | 61.52% | 10 |  | 0
|  |  | Flow Conversion Calculator | [5 empty] | General Info =
|  |  | MGD | 8.82 |  |  |  |  | Calculated =
| Test Pump Curve |  | GPM | 6125 |  |  |  |  | Manual Input from Pump Test =
Date:
Parameter | Test Pt 1 | Test Pt 2 | Test Pt 3 | Test Pt 4 | Test Pt 5 | Test Pt 6 | Test Pt 7 | Test Pt 8 | Test Pt 9 | Test Pt 10
Time:
Pump Speed (%)
Reservoir Level (ft):
Disch Press @ Pmp Flg. (psi):
Disch Press @ Header (psi):
Discharge Flow (mgd):
Amps 1:
Amps 2:
Amps 3:
Volts 1:
Volts 2:
Volts 3:
KW Input to Motor:
HP Input to Motor:
Ave. Amps
Ave. Volts
Total Head (ft):
Discharge Flow (gpm):
Overall Pump Efficiency:
FIELD TEST POINTS
Start Differential PSI 87 PSI 0 GPM
2nd Point Differential PSI 71 PSI 2146 GPM
3rd Point Differential PSI 66 PSI 3138 GPM
4th Point Differential PSI 59 PSI 4083 GPM
5th Point Differential PSI 57 PSI 4472 GPM
6th Point Differential PSI 54 PSI 5049 GPM
7th Point Differential PSI 52 PSI 5562 GPM
8th Point Differential PSI 51 PSI 6125 GPM
9th Point Differential PSI 40 PSI 7444 GPM
10th Point Differential PSI 24 PSI 8750 GPM

## SBFF Pump 2
Pump Station / No: | SBFFPS | #2 |  |  |  |  | Manufacturer Pump Curve |  |  |  | Test Pump Curve Transposed for Model Use
|  |  | Pump Mfr: | Peerless |  |  | TDH (ft) | Flow (mgd) | Flow (gpm) | Bowl Eff (%) | Test Pt | Total Head (ft): | Discharge Flow (mgd): | Overall Pump Efficiency:
Design Point |  |  | Pump Model: | 22BKL |  | 1 | 199.35 | 0 | 0 | 0% | 1 |  | 0
MGD | 8.0064 |  | Serial Number: | 78639-1-2 |  | 2 | 172.81 | 2.8638 | 1988.74 | 40.04% | 2 |  | 0
GPM | 5560 |  | Pump Installed: | 2018 |  | 3 | 154.21 | 4.3245 | 3003.1 | 55.88% | 3 |  | 0
TDH (FT) | 120 |  | Motor HP: | 250 |  | 4 | 136.97 | 5.7707 | 4007.46 | 67.59% | 4 |  | 0
|  |  | Motor Voltage: | 4160 |  | 5 | 129.2 | 6.501 | 4514.61 | 72.34% | 5 |  | 0
Elevation Information |  |  | Motor Installed: | 2018 |  | 6 | 124.59 | 7.2274 | 5019.01 | 77.12% | 6 |  | 0
Pump Disch Hdr CL Elev (ft): | 1473 |  | RPM: | 1785 |  | 7 | 121.41 | 8.0256 | 5573.35 | 81.75% | 7 |  | 0
Reservoir Floor Elev (ft): | 1444.5 |  | Power Factor: | 0.8 |  | 8 | 115.21 | 8.8095 | 6117.7 | 83.27% | 8 |  | 0
Suction Header CL Elev (ft): | NA |  | Motor Efficiency: | 0.9 |  | 9 | 90.56 | 10.6433 | 7391.18 | 79.9% | 9 |  | 0
Service Zone: | Falcon Field |  |  |  |  | 10 | 52.32 | 12.6643 | 8794.65 | 59.47% | 10 |  | 0
|  |  | Flow Conversion Calculator | [5 empty] | General Info =
|  |  | MGD | [5 empty] | Calculated =
| Test Pump Curve |  | GPM | 0 |  |  |  |  | Manual Input from Pump Test =
Date:
Parameter | Test Pt 1 | Test Pt 2 | Test Pt 3 | Test Pt 4 | Test Pt 5 | Test Pt 6 | Test Pt 7 | Test Pt 8 | Test Pt 9 | Test Pt 10
Time:
Pump Speed (%)
Reservoir Level (ft):
Disch Press @ Pmp Flg. (psi):
Disch Press @ Header (psi):
Discharge Flow (mgd):
Amps 1:
Amps 2:
Amps 3:
Volts 1:
Volts 2:
Volts 3:
KW Input to Motor:
HP Input to Motor:
Ave. Amps
Ave. Volts
Total Head (ft):
Discharge Flow (gpm):
Overall Pump Efficiency:
FIELD TEST POINTS
Start Differential PSI 86 PSI 0 GPM
2nd Point Differential PSI 75 PSI 1986 GPM
3rd Point Differential PSI 67 PSI 3000 GPM
4th Point Differential PSI 59 PSI 4007 GPM
5th Point Differential PSI 56 PSI 4514 GPM
6th Point Differential PSI 54 PSI 5021 GPM
7th Point Differential PSI 52 PSI 5563 GPM
8th Point Differential PSI 50 PSI 6118 GPM
9th Point Differential PSI 39 PSI 7389 GPM
10th Point Differential PSI 23 PSI 8792 GPM

## SBFF Pump 3
Pump Station / No: | SBFFPS | #3 |  |  |  |  | Manufacturer Pump Curve |  |  |  | Test Pump Curve Transposed for Model Use
|  |  | Pump Mfr: | Peerless |  |  | TDH (ft) | Flow (mgd) | Flow (gpm) | Bowl Eff (%) | Test Pt | Total Head (ft): | Discharge Flow (mgd): | Overall Pump Efficiency:
Design Point |  |  | Pump Model: | 22BKL |  | 1 | 202.54 | 0 | 0 | 0% | 1 |  | 0
MGD | 8.0064 |  | Serial Number: | 78639-1-3 |  | 2 | 164.15 | 2.9501 | 2048.65 | 39.59% | 2 |  | 0
GPM | 5560 |  | Pump Installed: | 2018 |  | 3 | 152.8 | 4.3891 | 3048 | 56.05% | 3 |  | 0
TDH (FT) | 120 |  | Motor HP: | 250 |  | 4 | 136.49 | 5.7418 | 3987.38 | 66.98% | 4 |  | 0
|  |  | Motor Voltage: | 4160 |  | 5 | 129.32 | 6.5333 | 4537.02 | 72.51% | 5 |  | 0
Elevation Information |  |  | Motor Installed: | 2018 |  | 6 | 125.83 | 7.1809 | 4986.72 | 76.48% | 6 |  | 0
Pump Disch Hdr CL Elev (ft): | 1473 |  | RPM: | 1785 |  | 7 | 122.42 | 8.0011 | 5556.35 | 80.88% | 7 |  | 0
Reservoir Floor Elev (ft): | 1444.5 |  | Power Factor: | 0.8 |  | 8 | 116.92 | 8.7998 | 6110.98 | 82.95% | 8 |  | 0
Suction Header CL Elev (ft): | NA |  | Motor Efficiency: | 0.9 |  | 9 | 91.59 | 10.6634 | 7405.13 | 79.05% | 9 |  | 0
Service Zone: | Falcon Field |  |  |  |  | 10 | 51.99 | 12.7141 | 8829.25 | 57.84% | 10 |  | 0
|  |  | Flow Conversion Calculator | [5 empty] | General Info =
|  |  | MGD | 12.71 |  |  |  |  | Calculated =
| Test Pump Curve |  | GPM | 8826.3889 |  |  |  |  | Manual Input from Pump Test =
Date:
Parameter | Test Pt 1 | Test Pt 2 | Test Pt 3 | Test Pt 4 | Test Pt 5 | Test Pt 6 | Test Pt 7 | Test Pt 8 | Test Pt 9 | Test Pt 10
Time:
Pump Speed (%)
Reservoir Level (ft):
Disch Press @ Pmp Flg. (psi):
Disch Press @ Header (psi):
Discharge Flow (mgd):
Amps 1:
Amps 2:
Amps 3:
Volts 1:
Volts 2:
Volts 3:
KW Input to Motor:
HP Input to Motor:
Ave. Amps
Ave. Volts
Total Head (ft):
Discharge Flow (gpm):
Overall Pump Efficiency:
FIELD TEST POINTS
Start Differential PSI 88 PSI 0 GPM
2nd Point Differential PSI 71 PSI 2049GPM
3rd Point Differential PSI 66 PSI 3049 GPM
4th Point Differential PSI 59 PSI 3986 GPM
5th Point Differential PSI 56 PSI 4472 GPM
6th Point Differential PSI 54 PSI 4986 GPM
7th Point Differential PSI 52 PSI 5563 GPM
8th Point Differential PSI 51 PSI 6111 GPM
9th Point Differential PSI 40 PSI 7403 GPM
10th Point Differential PSI 23 PSI 8826 GPM

## SBDW Pump 4
Pump Station / No: | SBDWPS | #4 |  |  |  | Manufacturer Pump Curve |  |  |  |  | Test Pump Curve 4/16/18 Transposed for Model Use
|  |  | Pump Mfr: | Floway |  | TDH (ft) | Flow (mgd) | Flow (gpm) | Bowl Eff (%) | Power (BHP) | Test Pt | Total Head (ft): | Discharge Flow (mgd): | Overall Pump Efficiency:
Design Point |  |  | Pump Model: | 27 FKH | 1 | 290.66 | 0 | 0 | 0% | 434.6 | 1 | 313.1828 | 0 | 0%
MGD | 11.0016 |  | Serial Number: | 78639-9-1 | 2 | 269.26 | 2.4768 | 1720.01 | 26.84% | 435.79 | 2 | 294.8121 | 1.3176 | 15.24%
GPM | 7640 |  | Pump Installed: | 2018 | 3 | 243.94 | 4.9681 | 3450.09 | 49.58% | 428.7 | 3 | 270.6503 | 3.7872 | 40.98%
TDH (FT) | 207 |  | Motor HP: | 500 | 4 | 226.53 | 7.4368 | 5164.41 | 66.46% | 443.87 | 4 | 252.1934 | 5.2632 | 53.44%
|  |  | Motor Voltage: | 4160 | 5 | 214.22 | 10.0632 | 6988.3 | 79.3% | 476.74 | 5 | 242.2894 | 6.6932 | 64.5%
Elevation Information |  |  | Motor Installed: | 2018 | 6 | 207.45 | 11.0869 | 7699.24 | 83.62% | 482.35 | 6 | 235.3194 | 7.4045 | 68.55%
Pump Disch Hdr CL Elev (ft): | 1473 |  | RPM: | 1190 | 7 | 194.26 | 12.2559 | 8511.01 | 86.24% | 484.13 | 7 | 223.8472 | 9.5285 | 80.1%
Reservoir Floor Elev (ft): | 1444.5 |  | Power Factor: | 0.8 | 8 | 178.58 | 13.403 | 9307.66 | 86.72% | 484.04 | 8 | 210.3352 | 11.618 | 89.41%
Suction Header CL Elev (ft): | NA |  | Motor Efficiency: | 0.92 | 9 | 159.22 | 14.5524 | 10105.82 | 85.22% | 476.8 | 9 | 191.1328 | 12.9327 | 90.02%
Service Zone: | Desert Wells |  | No. of Stages: | 2 | 10 | 139.97 | 15.5693 | 10812.03 | 82.05% | 465.73 | 10 |  | 0
|  |  | Impeller Trim: | 15.69" | 11 | 109.5 | 16.8453 | 11698.11 | 72.8% | 444.33
|  |  | Flow Conversion Calculator | [5 empty] | General Info =
|  |  | MGD | 16.85 |  |  |  |  | Calculated = |  |  | Try not to run less than 4,000 gpm
| Test Pump Curve |  | GPM | 11701.3889 |  |  |  |  | Manual Input from Pump Test = |  |  | Min Speed = 0.0022(TDH) + 0.48
Date: | 4/16/18
Parameter | Test Pt 1 | Test Pt 2 | Test Pt 3 | Test Pt 4 | Test Pt 5 | Test Pt 6 | Test Pt 7 | Test Pt 8 | Test Pt 9 | Test Pt 10 |  | TDH, ft | 155
Time: | [11 empty] | Min Speed | 0.821
Pump Speed (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Reservoir Level (ft): | 23.05 | 23.1 | 23.1 | 23.1 | 23.1 | 23.12 | 23.12 | 23.1 | 23.09 |  |  | % Speed | TDH
Disch Press @ Pmp Flg. (psi): | 133.2177 | 125.2866 | 114.827 | 106.837 | 102.5495 | 99.5409 | 94.5745 | 88.7165 | 80.3995 |  |  | 100% | 240
Disch Press @ Header (psi): | 58.5 | 58.2 | 52.4 | 66.2 | 64.2 | 67.4 | 66.2 | 71.7 | 70.2 |  |  | 91% | 200
Discharge Flow (mgd): | 0 | 1.3176 | 3.7872 | 5.2632 | 6.6932 | 7.4045 | 9.5285 | 11.618 | 12.9327 |  |  | 88% | 180
Amps 1: | 59 | 59.1 | 58 | 57.6 | 58.3 | 58.8 | 61.6 | 63.3 | 63.6 |  |  | 82% | 160
Amps 2: | 59 | 59.1 | 58 | 57.6 | 58.3 | 58.8 | 61.6 | 63.3 | 63.6 |  |  | 77% | 135
Amps 3: | 59 | 59.1 | 58 | 57.6 | 58.3 | 58.8 | 61.6 | 63.3 | 63.6
Volts 1: | 4070 | 4070 | 4070 | 4070 | 4070 | 4080 | 4080 | 4075 | 4075
Volts 2: | 4070 | 4070 | 4070 | 4070 | 4070 | 4080 | 4080 | 4075 | 4075
Volts 3: | 4070 | 4070 | 4070 | 4070 | 4070 | 4080 | 4080 | 4075 | 4075
KW Input to Motor: | 332.7241 | 333.2881 | 327.0847 | 324.829 | 328.7766 | 332.411 | 348.2401 | 357.4121 | 359.106
HP Input to Motor: | 446.1831 | 446.9393 | 438.6206 | 435.5957 | 440.8894 | 445.7631 | 466.9899 | 479.2896 | 481.5611
Ave. Amps 4/16/18 | 59 | 59.1 | 58 | 57.6 | 58.3 | 58.8 | 61.6 | 63.3 | 63.6
Ave. Volts 4/16/18 | 4070 | 4070 | 4070 | 4070 | 4070 | 4080 | 4080 | 4075 | 4075
Total Head (ft): | 313.1828 | 294.8121 | 270.6503 | 252.1934 | 242.2894 | 235.3194 | 223.8472 | 210.3352 | 191.1328
Discharge Flow (gpm): | 0 | 915.0059 | 2630.0168 | 3655.0234 | 4648.0297 | 5142.0329 | 6617.0423 | 8068.0516 | 8981.0575
Overall Pump Efficiency: | 0% | 15.24% | 40.98% | 53.44% | 64.5% | 68.55% | 80.1% | 89.41% | 90.02%
FIELD TEST POINTS
Start Differential PSI 126 PSI 0 GPM
2nd Point Differential PSI 117 PSI 1722 GPM
3rd Point Differential PSI 106 PSI 3451 GPM
4th Point Differential PSI 98 PSI 5167 GPM
5th Point Differential PSI 93 PSI 7361 GPM
6th Point Differential PSI 90 PSI 7638 GPM
7th Point Differential PSI 84 PSI 8514 GPM
8th Point Differential PSI 77 PSI 9306 GPM
9th Point Differential PSI 61 PSI 10812 GPM
10th Point Differential PSI 47 PSI 11701 GPM

## SBDW Pump 5
Pump Station / No: | SBDWPS | #5 |  |  |  | Manufacturer Pump Curve |  |  |  |  | Test Pump Curve 4/16/18 Transposed for Model Use
|  |  | Pump Mfr: | Floway |  | TDH (ft) | Flow (mgd) | Flow (gpm) | Bowl Eff (%) | Power (BHP) | Test Pt | Total Head (ft): | Discharge Flow (mgd): | Overall Pump Efficiency:
Design Point |  |  | Pump Model: | 27 FKH | 1 | 290.66 | 0 | 0 | 0% | 434.6 | 1 | 359.222 | 0 | 0%
MGD | 11.0016 |  | Serial Number: | 78639-9-2 | 2 | 269.26 | 2.4768 | 1720.01 | 26.84% | 435.79 | 2 | 294.763 | 1.3176 | 15.24%
GPM | 7640 |  | Pump Installed: | 2018 | 3 | 243.94 | 4.9681 | 3450.09 | 49.58% | 428.7 | 3 | 270.488 | 3.7872 | 40.96%
TDH (FT) | 207 |  | Motor HP: | 500 | 4 | 226.53 | 7.4368 | 5164.41 | 66.46% | 443.87 | 4 | 252.008 | 5.2632 | 53.4%
|  |  | Motor Voltage: | 4160 | 5 | 214.22 | 10.0632 | 6988.3 | 79.3% | 476.74 | 5 | 242.055 | 6.6932 | 64.44%
Elevation Information |  |  | Motor Installed: | 2018 | 6 | 207.45 | 11.0869 | 7699.24 | 83.62% | 482.35 | 6 | 235.125 | 7.4045 | 68.49%
Pump Disch Hdr CL Elev (ft): | 1473 |  | RPM: | 1190 | 7 | 194.26 | 12.2559 | 8511.01 | 86.24% | 484.13 | 7 | 223.575 | 9.5285 | 80%
Reservoir Floor Elev (ft): | 1444.5 |  | Power Factor: | 0.8 | 8 | 178.58 | 13.403 | 9307.66 | 86.72% | 484.04 | 8 | 210.197 | 11.618 | 89.35%
Suction Header CL Elev (ft): | NA |  | Motor Efficiency: | 0.92 | 9 | 159.22 | 14.5524 | 10105.82 | 85.22% | 476.8 | 9 | 195.674 | 12.9327 | 92.15%
Service Zone: | Desert Wells |  | No. of Stages: | 2 | 10 | 139.97 | 15.5693 | 10812.03 | 82.05% | 465.73 | 10 |  | 0
|  |  | Impeller Trim: | 15.69" | 11 | 109.5 | 16.8453 | 11698.11 | 72.8% | 444.33
|  |  | Flow Conversion Calculator | [5 empty] | General Info =
|  |  | MGD | 16.85 |  |  |  |  | Calculated =
| Test Pump Curve |  | GPM | 11701.3889 |  |  |  |  | Manual Input from Pump Test =
Date: | 4/16/18
Parameter | Test Pt 1 | Test Pt 2 | Test Pt 3 | Test Pt 4 | Test Pt 5 | Test Pt 6 | Test Pt 7 | Test Pt 8 | Test Pt 9 | Test Pt 10
Time:
Pump Speed (%) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Reservoir Level (ft): | 23.17 | 23.18 | 23.2 | 23.2 | 23.22 | 23.22 | 23.22 | 23.2 | 23.17
Disch Press @ Pmp Flg. (psi): | 153.2 | 125.3 | 114.8 | 106.8 | 102.5 | 99.5 | 94.5 | 88.7 | 82.4
Disch Press @ Header (psi): | 59.35 | 61.2 | 59.9 | 66.2 | 64.9 | 65.2 | 72.1 | 69.9 | 71.9
Discharge Flow (mgd): | 0 | 1.3176 | 3.7872 | 5.2632 | 6.6932 | 7.4045 | 9.5285 | 11.618 | 12.9327
Amps 1: | 59 | 59.1 | 58 | 57.6 | 58.3 | 58.8 | 61.6 | 63.3 | 63.6
Amps 2: | 59 | 59.1 | 58 | 57.6 | 58.3 | 58.8 | 61.6 | 63.3 | 63.6
Amps 3: | 59 | 59.1 | 58 | 57.6 | 58.3 | 58.8 | 61.6 | 63.3 | 63.6
Volts 1: | 4070 | 4070 | 4070 | 4070 | 4070 | 4080 | 4080 | 4075 | 4075
Volts 2: | 4070 | 4070 | 4070 | 4070 | 4070 | 4080 | 4080 | 4075 | 4075
Volts 3: | 4070 | 4070 | 4070 | 4070 | 4070 | 4080 | 4080 | 4075 | 4075
KW Input to Motor: | 332.7241 | 333.2881 | 327.0847 | 324.829 | 328.7766 | 332.411 | 348.2401 | 357.4121 | 359.106
HP Input to Motor: | 446.1831 | 446.9393 | 438.6206 | 435.5957 | 440.8894 | 445.7631 | 466.9899 | 479.2896 | 481.5611
Ave. Amps 4/16/18 | 59 | 59.1 | 58 | 57.6 | 58.3 | 58.8 | 61.6 | 63.3 | 63.6
Ave. Volts 4/16/18 | 4070 | 4070 | 4070 | 4070 | 4070 | 4080 | 4080 | 4075 | 4075
Total Head (ft): | 359.222 | 294.763 | 270.488 | 252.008 | 242.055 | 235.125 | 223.575 | 210.197 | 195.674
Discharge Flow (gpm): | 0 | 915.0059 | 2630.0168 | 3655.0234 | 4648.0297 | 5142.0329 | 6617.0423 | 8068.0516 | 8981.0575
Overall Pump Efficiency: | 0% | 15.24% | 40.96% | 53.4% | 64.44% | 68.49% | 80% | 89.35% | 92.15%
FIELD TEST POINTS
Start Differential PSI 126 PSI 0 GPM
2nd Point Differential PSI 117 PSI 1722 GPM
3rd Point Differential PSI 106 PSI 3451 GPM
4th Point Differential PSI 98 PSI 5167 GPM
5th Point Differential PSI 93 PSI 6986 GPM
6th Point Differential PSI 90 PSI 7639 GPM
7th Point Differential PSI 84 PSI 8514 GPM
8th Point Differential PSI 77 PSI 9306 GPM
9th Point Differential PSI 61 PSI 10813 GPM
10th Point Differential PSI 47 PSI 11701 GPM